## 表格_20260805
Name | Parameters
Product Name | Inedge Pod DB215 | Inedge Pod DB232
DC Side
Battery Type | LFP, 280Ah, 3.2Vdc
Battery Configuration | 1P48S*5S | 1P52S*5S
Rated Voltage | 768Vdc | 832Vdc
Voltage Range | 660~864Vdc | 715~936Vdc
Rated Energy | 215kWh | 232kWh
Rated Power | 0.5CP
AC Side
Rated Voltage | 400Vac
Rated Power | 105kW
Maximum Power | 115.5kW
AC Output Type | 3P+N+PE (N terminal reserved)
Isolation Method | Non‑isolated
Grid Frequency | 50/60Hz
Grid‑tied & Off‑grid Function | Grid‑tied and off‑grid
Surge Protection Device | Type 2
System
Weight | 2400kg | 2650kg
Dimension (WDH) | 103514002350mm
Operating Temperature | -30 ~ 50°C (>45°C, derating)
IP Rating | IP55, Outdoor
Protection Class | C4 (Max C5)
Cooling Method | Intelligent Liquid Cooling
Fire System ‑ Detector | Smoke detector, temperature detector, combustible gas detector
Fire System ‑ Explosion‑proof | Explosion‑proof ventilation
Fire System ‑ Fire Suppression | Module: Aerosol; System: Aerosol + Water‑based fire‑fighting pipeline
Fire System ‑ Alarm | Audible‑visual alarm
Battery Management System | 5BMU +1 BCMU | 5BMU +1 BCMU
Communication Method | LAN, CAN, RS485, I/O
Certification
Certification Standard | GB/T 36276, GB/T 34120, GB/T 34131